## University of San Diego-1
Customer: | University of San Diego
Size (kW): | 1000
Name: | University of San Diego
Location: | 5998 Alcala Park, San Diego, CA
University of San Diego
Date (Local) | Total Output Factor | AC Efficiency (LHV) | Heat Rate (HHV) | Electricity Out | Gas Flow In | Gas Flow In | CO₂ Reduction | CO₂ Production | NOₓ Reduction | NOₓ Production | SO₂ Reduction | SO₂ Production
| % | % | BTU/kWh | kWh | Therms | MMBtu | lbs | lbs | lbs | lbs | lbs | lbs
30-Day | 88.4% | 53.44% | 7071.932 | 624104 | 44136.2104 | 4413.621 | 179590.0175 | 516222.1511 | 509.9283 | 1.061 | 36.1667 | 0.0037134
Date (Local) | Total Output Factor | AC Efficiency (LHV) | Heat Rate (HHV) | Electricity Out | Gas Flow In | Gas Flow In | CO₂ Reduction | CO₂ Production | NOₓ Reduction | NOₓ Production | SO₂ Reduction | SO₂ Production
| % | % | BTU/kWh | kWh | Therms | MMBtu | lbs | lbs | lbs | lbs | lbs | lbs
2024-11-06 | 85.65% | 53.58% | 7053.4089 | 20556 | 1449.8987 | 144.9899 | 5957.3183 | 16960.5206 | 16.7954 | 0.034945 | 1.1912 | 0.00012231
2024-11-07 | 85.6% | 53.55% | 7056.7522 | 20544 | 1449.7392 | 144.9739 | 5945.8061 | 16958.654 | 16.7856 | 0.034925 | 1.1905 | 0.00012224
2024-11-08 | 82.03% | 53.28% | 7092.3115 | 19688 | 1396.3343 | 139.6334 | 5687.3867 | 16262.721 | 16.0862 | 0.03347 | 1.1409 | 0.00011714
2024-11-09 | 90.58% | 53.82% | 7022.1423 | 21740 | 1526.6137 | 152.6614 | 6379.9663 | 17857.9116 | 17.7628 | 0.036958 | 1.2598 | 0.00012935
2024-11-10 | 90.43% | 53.72% | 7034.3443 | 21704 | 1526.7341 | 152.6734 | 6338.4222 | 17859.3194 | 17.7334 | 0.036897 | 1.2577 | 0.00012914
2024-11-11 | 90.4% | 53.7% | 7036.9854 | 21696 | 1526.7443 | 152.6744 | 6329.3829 | 17859.4395 | 17.7269 | 0.036883 | 1.2573 | 0.00012909
2024-11-12 | 90.22% | 53.59% | 7051.3422 | 21652 | 1526.7566 | 152.6757 | 6280.1838 | 17859.5831 | 17.6909 | 0.036808 | 1.2547 | 0.00012883
2024-11-13 | 90.3% | 53.64% | 7044.8215 | 21672 | 1526.7537 | 152.6754 | 6302.5157 | 17859.5491 | 17.7073 | 0.036842 | 1.2559 | 0.00012895
2024-11-14 | 90.28% | 53.63% | 7046.8717 | 21668 | 1526.9162 | 152.6916 | 6296.1559 | 17861.4493 | 17.704 | 0.036836 | 1.2557 | 0.00012892
2024-11-15 | 90.23% | 53.59% | 7051.9535 | 21656 | 1527.1711 | 152.7171 | 6279.7955 | 17864.431 | 17.6942 | 0.036815 | 1.255 | 0.00012885
2024-11-16 | 90.27% | 53.61% | 7049.492 | 21664 | 1527.202 | 152.7202 | 6288.3531 | 17864.7925 | 17.7007 | 0.036829 | 1.2554 | 0.0001289
2024-11-17 | 90.3% | 53.63% | 7047.1009 | 21672 | 1527.2477 | 152.7248 | 6296.7372 | 17865.3277 | 17.7073 | 0.036842 | 1.2559 | 0.00012895
2024-11-18 | 90.3% | 53.62% | 7047.7435 | 21672 | 1527.387 | 152.7387 | 6295.1081 | 17866.9567 | 17.7073 | 0.036842 | 1.2559 | 0.00012895
2024-11-19 | 90.28% | 53.61% | 7048.8263 | 21668 | 1527.3397 | 152.734 | 6291.2017 | 17866.4036 | 17.704 | 0.036836 | 1.2557 | 0.00012892
2024-11-20 | 90.28% | 53.61% | 7048.8272 | 21668 | 1527.3399 | 152.734 | 6291.1994 | 17866.4059 | 17.704 | 0.036836 | 1.2557 | 0.00012892
2024-11-21 | 90.25% | 53.59% | 7051.4641 | 21660 | 1527.3471 | 152.7347 | 6282.1953 | 17866.4908 | 17.6974 | 0.036822 | 1.2552 | 0.00012888
2024-11-22 | 90.2% | 53.56% | 7056.1145 | 21648 | 1527.5077 | 152.7508 | 6266.9386 | 17868.3687 | 17.6876 | 0.036802 | 1.2545 | 0.00012881
2024-11-23 | 90.12% | 53.51% | 7062.6761 | 21628 | 1527.5156 | 152.7516 | 6244.548 | 17868.4613 | 17.6713 | 0.036768 | 1.2533 | 0.00012869
2024-11-24 | 90.02% | 53.45% | 7070.2362 | 21604 | 1527.4538 | 152.7454 | 6218.5129 | 17867.7389 | 17.6517 | 0.036727 | 1.2519 | 0.00012854
2024-11-25 | 88.73% | 53.42% | 7073.9302 | 21296 | 1506.4642 | 150.6464 | 6120.6556 | 17622.2077 | 17.4 | 0.036203 | 1.2341 | 0.00012671
2024-11-26 | 87.87% | 53.14% | 7111.6829 | 21088 | 1499.7117 | 149.9712 | 5967.7456 | 17543.2189 | 17.2301 | 0.03585 | 1.222 | 0.00012547
2024-11-27 | 66.6% | 51.2% | 7381.1993 | 15984 | 1179.8109 | 117.9811 | 4019.4197 | 13801.1065 | 13.0598 | 0.027173 | 0.92627 | 9.5105e-05
2024-11-28 | 89.23% | 53.33% | 7086.185 | 21416 | 1517.5774 | 151.7577 | 6124.4441 | 17752.2069 | 17.4981 | 0.036407 | 1.2411 | 0.00012743
2024-11-29 | 89.27% | 53.36% | 7082.2639 | 21424 | 1517.3042 | 151.7304 | 6136.5586 | 17749.0116 | 17.5046 | 0.036421 | 1.2415 | 0.00012747
2024-11-30 | 89.25% | 53.35% | 7083.5849 | 21420 | 1517.3039 | 151.7304 | 6132.1029 | 17749.0077 | 17.5014 | 0.036414 | 1.2413 | 0.00012745
2024-12-01 | 89.18% | 53.31% | 7088.8181 | 21404 | 1517.2906 | 151.7291 | 6114.4199 | 17748.8524 | 17.4883 | 0.036387 | 1.2404 | 0.00012735
2024-12-02 | 89.18% | 53.29% | 7091.6428 | 21404 | 1517.8952 | 151.7895 | 6107.3473 | 17755.9249 | 17.4883 | 0.036387 | 1.2404 | 0.00012735
2024-12-03 | 88.9% | 53.2% | 7103.8963 | 21336 | 1515.6873 | 151.5687 | 6057.3618 | 17730.0973 | 17.4327 | 0.036271 | 1.2364 | 0.00012695
2024-12-04 | 88.62% | 53.29% | 7091.0627 | 21268 | 1508.1272 | 150.8127 | 6069.9846 | 17641.6615 | 17.3772 | 0.036156 | 1.2325 | 0.00012654
2024-12-05 | 86.04% | 53.39% | 7078.5153 | 8604 | 609.0355 | 60.9035 | 2468.2497 | 7124.3309 | 7.03 | 0.014627 | 0.4986 | 5.1194e-05

## Definition
Description of Data Fields
Total Output Factor (%) | Total system output calculated by dividing actual power output over a given period of time by the potential power output while operating at name plate capacity
AC Efficiency (%, LHV) | Energy output per energy input calculated as LHV efficiency based on LHV to HHV, kWh to BTU, and Therms to BTU conversion ratios
Heat Rate (BTU/kWh, HHV) | Heat rate is calculated as BTU/kWh
Electricity Out (kWh) | Amount of electricity produced; measured at the transformer and after the inverter, in the electrical connection (480V @ 60Hz, 4-wire 3 phase)
Gas Flow In (Therms, MMBtu) | Heat energy measurement of consumed fuel
CO₂ Reduction (lbs) | Amount of CO₂ avoided by using Bloom Energy Servers for electricity compared to the power grid in the state in which the project is located; calculated by multiplying kWh generated by the difference between the state's marginal rate of emissions and Bloom Energy Server's rate of emissions
AC Efficiency Calculation Formula (LHV)